## _Index
SPUR Combined Model (v7 + Model 3)
MODEL 2: Project-Level DCF (Developer IRR)
Inputs | Global scenario levers (queue wait, ITC, credit type) + shared parameters
Configurations | Per-configuration CAPEX, CF, degradation, operating life (Solar/Wind/Geo)
Capitalization | Tax equity / debt / developer equity sizing: 6 columns (Base+Coloc × 3 configs)
SolarBase | Solar+BESS 100MW cash flow waterfall: project idle during queue wait
SolarColoc | Solar+BESS 100MW cash flow waterfall: BTM sales during queue wait
WindBase | Wind+BESS 150MW cash flow waterfall: project idle during queue wait
WindColoc | Wind+BESS 150MW cash flow waterfall: BTM sales during queue wait
GeoBase | Geothermal+BESS 100MW cash flow waterfall: project idle during queue wait
GeoColoc | Geothermal+BESS 100MW cash flow waterfall: BTM sales during queue wait
Results | Live IRR/NPV/Value Bridge + Queue×ITC sweep tables (all 3 configs)
MODEL 3: Data Center Electricity Cost (H2 Test)
M3_Inputs | DC load, generation supply, sourced & placeholder prices
M3_Coverage | Energy-balance coverage ratio by configuration
M3_StructA_B | Structure A (utility tariff) & Structure B (sleeved grid PPA) all-in cost
M3_StructC | Structure C (BTM co-location) Phase 1 & Phase 2 all-in cost
M3_Results | Cost comparison + H2 savings test (20-35% threshold)
MODEL 1: Electricity Price Benchmark (Stage 1)
M1_Inputs | All DMM-sourced data points (annual, quarterly, hourly, GHG) with URL citations
M1_Benchmarks | Derivation of P_low / P_avg / P_high from DMM hourly & annual statistics
M1_Scenarios | 3×3 matrix (load × carbon) = 9 price scenarios; spot-to-PPA bridge; solar capture caveat
M1_Notes | Methodology: why DMM instead of raw OASIS, binning proxy, limitations, replication path
MODEL 4: Bilateral BTM PPA Pricing (Negotiation Zone)
M4_LCOE | LCOE per configuration (gross & net of tax equity): the developer's price floor
M4_Bounds | Floor vs three ceilings (all-in / energy-only / spot+wires); zone width; viability tests
M4_Pricing | Three price-setting methods; α lever; two-sided test; analytical mutually-acceptable range
M4_Notes | Methodology, findings (incl. $60 < LCOE for solar/wind), open loop-closure items
FIGURES (native Excel charts; data + chart on each sheet)
Fig2_Breakeven | Levered IRR vs queue wait, 6 panels (lever × config); static sweep values
Fig3_Zone | Price floor / ceiling / acceptable range stacked bar; LIVE links to M4
Fig4_Alpha | IRR and DC saving vs bargaining share α, 3 panels; static sweep values

## M1_Inputs
Model 1: Electricity Price Benchmark: INPUTS (CAISO DMM Published Statistics)
Blue = hardcoded from published DMM reports. Every value carries a source + URL in column E. See M1_Notes for methodology deviation from original Stage 1 spec.
SEC 1: ANNUAL LOAD-WEIGHTED AVERAGE PRICES: California region
Parameter | Value | Unit | Year | Source
CA region day-ahead market avg price | 41 | $/MWh | 2024 | CAISO DMM 2024 Annual Report (Aug 7, 2025), Executive Summary p.3: 'day-ahead market prices averaged $41/MWh'. https://www.caiso.com/documents/2024-annual-report-on-market-issues-and-performance-aug-07-2025.pdf
CA region 15-min market avg price | 41.1 | $/MWh | 2024 | CAISO DMM 2024 Annual Report, Figure E.2 table: California 41.1, -36% vs 2023. Same URL.
CA region day-ahead market avg price | 39 | $/MWh | 2025 | CAISO DMM 2025 Annual Report (Jun 26, 2026), Executive Summary p.3: 'Day-ahead market prices averaged about $39/MWh'. https://www.caiso.com/documents/2025-annual-report-on-market-issues-and-performance.pdf
CA region 15-min market avg price | 38.32 | $/MWh | 2025 | CAISO DMM 2025 Annual Report, Figure E.2 table: California $38.32, -7% vs 2024. Same URL.
CAISO total wholesale cost per MWh of load | 42 | $/MWh | 2025 | CAISO DMM 2025 Annual Report, p.4: 'Total wholesale costs for the CAISO balancing area decreased by about 6 percent to $8.45 billion, or about $42/MWh'. Same URL.
Implied 2023 CA DA avg (back-calc from -36% YoY) | 64.2188 | $/MWh | 2023 | Calc: 2024 value / (1 - 0.36). DMM 2024 Annual Report states CA prices fell 36% from 2023. Use as high-gas-price sensitivity only.
SEC 2: QUARTERLY PRICES: seasonal shape (CAISO balancing area)
Parameter | Value | Unit | Year | Source
Q1 2024 avg (DA/15-min/5-min blended) | 43 | $/MWh | 2024 Q1 | CAISO DMM Q1 2024 Report (Oct 11, 2024): 'average price of the three markets this quarter decreased to $43/MWh from $93/MWh in Q1 2023'. https://www.caiso.com/documents/2024-first-quarter-report-on-market-issues-and-performance-oct-11-2024.pdf
Q2 2024 avg (15-min, WEIM-wide) | 19 | $/MWh | 2024 Q2 | CAISO DMM Q2 2024 Report (Nov 22, 2024): 'Prices in both the 15-minute and 5-minute markets averaged around $19/MWh, down 40% vs Q2 2023'. WEIM-wide figure; CA-specific likely ~$5-8 higher due to GHG. https://www.caiso.com/documents/2024-second-quarter-report-on-market-issues-and-performance-nov-22-2024.pdf
Q3 2024 CAISO day-ahead avg | 48 | $/MWh | 2024 Q3 | CAISO DMM Q3 2024 Report (Dec 23, 2024), Sec 3.3 p.27: 'day-ahead prices averaged $48/MWh, 15-minute $47/MWh, 5-minute $40/MWh'. https://www.caiso.com/documents/2024-third-quarter-report-on-market-issues-and-performance-dec-23-2024.pdf
Q3 2024 CA region 15-min avg | 47.5 | $/MWh | 2024 Q3 | CAISO DMM Q3 2024 Report, Figure E.1 table: California 47.5, -27% vs Q3 2023. Same URL.
Q3 2024 July monthly DA peak-hours avg | 58 | $/MWh | 2024 Jul | CAISO DMM Q3 2024 Report, Figure 3.12 table: CAISO Jul $58 / Aug $42 / Sep $40 (peak hours HE7-22). Same URL.
Q4 2025 WEIM 15-min avg | 36 | $/MWh | 2025 Q4 | CAISO DMM Q4 2025 Report (Mar 30, 2026): 'Overall 15-minute market prices across WEIM averaged $36/MWh, down 7% vs Q4 2024'. https://www.caiso.com/documents/2025-fourth-quarter-report-on-market-issues-and-performance.pdf
SEC 3: HOURLY 15-MIN MARKET PRICES: Q3 2024 (Jul–Sep), CAISO DLAPs
Source: CAISO DMM Q3 2024 Report, Table 3.3 'Hourly 15-minute market prices (July–September)', p.26. Values are load-weighted hourly averages at PG&E and SCE default load aggregation points. Same URL as SEC 2 Q3 row.
Hour Ending | PG&E DLAP ($/MWh) | SCE DLAP ($/MWh) | Blend ($/MWh) | Net-load regime
1 | 40 | 40 | 40 | Overnight
2 | 38 | 38 | 38 | Overnight
3 | 36 | 36 | 36 | Overnight
4 | 35 | 35 | 35 | Overnight
5 | 35 | 35 | 35 | Overnight
6 | 39 | 38 | 38.5 | Overnight
7 | 40 | 40 | 40 | Overnight
8 | 32 | 30 | 31 | Morning ramp
9 | 27 | 21 | 24 | Mid-day solar
10 | 26 | 19 | 22.5 | Mid-day solar
11 | 25 | 20 | 22.5 | Mid-day solar
12 | 27 | 21 | 24 | Mid-day solar
13 | 27 | 23 | 25 | Mid-day solar
14 | 29 | 24 | 26.5 | Mid-day solar
15 | 31 | 27 | 29 | Mid-day solar
16 | 40 | 33 | 36.5 | Evening ramp
17 | 45 | 36 | 40.5 | Evening ramp
18 | 60 | 48 | 54 | Evening ramp
19 | 91 | 77 | 84 | Evening peak
20 | 119 | 104 | 111.5 | Evening peak
21 | 75 | 65 | 70 | Evening peak
22 | 56 | 53 | 54.5 | Late evening
23 | 46 | 45 | 45.5 | Late evening
24 | 42 | 42 | 42 | Late evening
SEC 4: GREENHOUSE GAS PRICE & IMPLIED MARGINAL EMISSION RATE
Parameter | Value | Unit | Year | Source
CA GHG allowance price (bilateral avg) | 38.09 | $/mtCO2e | 2024 | CAISO DMM 2024 Annual Report, p.2: 'California greenhouse gas allowances averaged $38.09/mtCO2e in bilateral markets in 2024'.
GHG cost impact on efficient gas unit | 16.19 | $/MWh | 2024 | CAISO DMM 2024 Annual Report, p.2: 'This represented an additional cost of about $16.19/MWh for a relatively efficient gas unit'.
CA GHG allowance price (bilateral avg) | 29.89 | $/mtCO2e | 2025 | CAISO DMM 2025 Annual Report, p.2: 'California greenhouse gas allowance prices averaged about $29.89/mtCO2e in 2025, down 22 percent from 2024'.
GHG cost impact on efficient gas unit | 12.7 | $/MWh | 2025 | CAISO DMM 2025 Annual Report, p.2: 'representing an incremental cost of about $12.70/MWh for a relatively efficient gas unit'.
Implied marginal emission rate (2024) | 0.42505 | tCO2e/MWh | 2024 | Calc: $/MWh ÷ $/mtCO2e. DMM-implied heat rate for 'relatively efficient gas unit' (CCGT). Cross-check: framework Sec 1.2 assumed 0.4–0.6 t/MWh.
Implied marginal emission rate (2025) | 0.42489 | tCO2e/MWh | 2025 | Calc: same method. Consistency across years validates the DMM heat-rate assumption.
Marginal emission rate: model input | 0.42497 | tCO2e/MWh | avg | Calc: average of 2024 and 2025 implied rates. Used for carbon overlay in M1_Scenarios.
SEC 5: PRICE DISTRIBUTION CONTEXT: tail behavior
Parameter | Value | Unit | Year | Source
Hours with negative DA price (SP15) | 1180 | hours/yr | 2024 | Resurety, 'Negative Prices in CAISO' (May 2025): '~1,180 hours in 2024 had below-zero prices (~13% of total hours)'. https://resurety.com/article-negative-prices-in-caiso/
Share of hours negative | 13.47% | frac | 2024 | Calc: hours / 8760
Median negative price (SP15) | -17 | $/MWh | 2024 | Resurety (May 2025): 'median negative price in 2024 was ~-$17'. Same URL.
Solar capture rate SP15 | 30% | frac of ATC | 2024 | Resurety (May 2025): 'annual solar capture rates to plummet to less than 30% in 2024' in SP15. Same URL. CRITICAL for solar config revenue assumption in Model 2.
DA intervals with price > $250/MWh | 0.6% | frac | 2024 Q3 | CAISO DMM Q3 2024 Report, Sec 3.5 p.33: 'day-ahead market recorded 0.6 percent of intervals with average price exceeding $250/MWh'.
Max DA (IFM) price observed | 637 | $/MWh | 2024 Sep 5 | CAISO Summer Market Performance Report Sep 2024 (Oct 31, 2024): 'IFM reached a maximum of $637/MWh on September 5'. https://www.caiso.com/documents/summer-market-performance-report-september-2024.pdf
HE20 DA load-weighted avg (Q3 2024) | 120 | $/MWh | 2024 Q3 | CAISO DMM Q3 2024 Report, Sec 3.3 p.29: 'During hour-ending 20, the day-ahead load-weighted average energy price was $120/MWh'.

## M1_Benchmarks
Model 1: Three Load-Level Price Benchmarks (derived from DMM hourly & annual statistics)
Green = pulled from M1_Inputs. Black = formula. Yellow = headline benchmark output feeding M1_Scenarios. Hour-bin definitions are a judgment call: see M1_Notes §3.
SEC 1: HOUR-BIN DEFINITIONS (mapping framework load percentiles → DMM hourly regime)
Benchmark | Framework definition | DMM proxy (Q3 2024 Table 3.3 hours) | Hours in bin | Rationale
LOW | Bottom 20th pctile system load; spring shoulder, mild weather, high solar | HE10–HE13 (mid-day solar trough) | 10,11,12,13 | Framework text describes high-solar hours, i.e. low NET load. Mid-day trough is the empirical minimum in DMM Table 3.3 and the regime where solar/wind projects would actually be selling. Overnight hours (HE1-7, ~$35-40) are low GROSS load but not the framework's intent.
AVERAGE | 30th–70th pctile system load; typical demand, moderate weather | Annual load-weighted DA average (2024 & 2025) | all 8,760 | Load-weighted annual mean already integrates the full distribution; DMM publishes this directly. Two-year average dampens single-year gas-price idiosyncrasy (2024 unusually low gas).
HIGH | Top 10th pctile system load; summer peak, extreme heat, evening ramp | HE19–HE21 (evening net-load peak) | 19,20,21 | DMM Q3 2024 confirms 'prices peaked at HE20 when demand was still high but solar substantially below its peak'. Summer evening ramp is top-decile net load. Excludes extreme scarcity tail (>$250, only 0.6% of Q3 intervals).
SEC 2: LOW BENCHMARK: mid-day solar trough
PG&E DLAP, HE10–13 avg | 26.25 | $/MWh
SCE DLAP, HE10–13 avg | 20.75 | $/MWh
Blended (equal weight PG&E/SCE) | 23.5 | $/MWh
Cross-check: Q2 2024 WEIM 15-min avg | 43 | $/MWh | Spring-shoulder quarterly avg; WEIM-wide so ~$5–8 below CA. Consistent with mid-day blend.
Cross-check: framework prior range | 15 – 30 | $/MWh | Framework Sec 1.2 expected range. Blended value falls inside.
LOW BENCHMARK (P_low) | 24 | $/MWh | Rounded to nearest $1. Mid-day Q3 blend; Q3 is the season where mid-day solar depression is strongest, so this is a conservative (low) value for annual mid-day.
SEC 3: AVERAGE BENCHMARK: annual load-weighted DA
2024 CA DA avg | 41 | $/MWh
2025 CA DA avg | 39 | $/MWh
2-year average | 40 | $/MWh
Cross-check: 2023 implied (high gas year) | 64.2188 | $/MWh | Excluded from base benchmark: 2023 gas prices were anomalously high (SoCal Citygate $5.12 vs $2.14 in 2024). Available as upside sensitivity.
Cross-check: framework prior range | 35 – 55 | $/MWh | Framework Sec 1.2. 2-yr average falls inside.
AVERAGE BENCHMARK (P_avg) | 40 | $/MWh | Rounded to nearest $1.
SEC 4: HIGH BENCHMARK: summer evening net-load peak
PG&E DLAP, HE19–21 avg | 95 | $/MWh
SCE DLAP, HE19–21 avg | 82 | $/MWh
Blended (equal weight PG&E/SCE) | 88.5 | $/MWh
Cross-check: HE20 DA load-weighted (Q3 2024) | 120 | $/MWh | Single peak hour; DA slightly above 15-min in this hour. Blend of HE19-21 is the fairer top-decile representation.
Cross-check: framework prior range | 60 – 120 | $/MWh | Framework Sec 1.2. Blended value falls inside.
HIGH BENCHMARK (P_high) | 89 | $/MWh | Rounded to nearest $1. Q3-only; represents the summer regime where top-decile load occurs.
SEC 5: SUMMARY: three base benchmarks (feed M1_Scenarios)
Benchmark | $/MWh | vs. P_avg | Framework range | Inside range?
P_low | 24 | -40% | $15–$30 | YES
P_avg | 40 | 0% | $35–$55 | YES
P_high | 89 | 122.5% | $60–$120 | YES

## M1_Scenarios
Model 1: Nine Price Scenarios (3 load levels × 3 carbon prices) + PPA Bridge
This is the Stage 1 output. Carbon adders are INCREMENTAL to the CA cap-and-trade cost already embedded in observed prices (framework Sec 1.2: '$0/ton = status quo').
SEC 1: CARBON OVERLAY PARAMETERS
Marginal emission rate (DMM-implied, efficient CCGT) | 0.42497 | tCO2e/MWh | From M1_Inputs SEC 4. Framework assumed 0.4–0.6; DMM data pins it at the low end (efficient CCGT sets the margin).
Already-embedded CA carbon cost (2025 avg) | 29.89 | $/tCO2e | Context only: observed prices already include this. Scenario adders stack on top.
Carbon scenario | Incremental $/tCO2e | Adder $/MWh | Framework rationale
C0: status quo | 0 | 0 | Current CA cap-and-trade only (already in observed prices)
C30: moderate | 30 | 12.7491 | Framework Sec 1.2: cap-and-trade escalation or federal carbon tax
C60: aggressive | 60 | 25.4981 | Framework Sec 1.2: aggressive decarbonization / high SCC
SEC 2: NINE-SCENARIO PRICE MATRIX ($/MWh): STAGE 1 OUTPUT
Load level ↓ / Carbon → | C0: status quo | C30: moderate | C60: aggressive
LOW (mid-day solar trough) | 24 | 36.7491 | 49.4981
AVERAGE (annual load-wtd) | 40 | 52.7491 | 65.4981
HIGH (evening net-load peak) | 89 | 101.7491 | 114.4981
Scenario naming for Model 2/3/4 runs: {L,A,H} × {C0,C30,C60} → e.g. 'A-C0' = average load, status-quo carbon = base case.
SEC 3: SPOT-TO-PPA BRIDGE: how Model 1 connects to the $72/MWh already in Model 2
Model 2 v7 uses a $72/MWh hybrid (solar+storage) PPA price sourced from LBNL Utility-Scale Solar. A PPA is a 15–20 yr fixed-price forward contract; spot DA prices are the annual realized average. The two are not the same quantity. This block reconciles them so the paper can state the relationship explicitly.
Model 2 grid PPA price (LBNL hybrid PPA) | 72 | $/MWh | Cross-sheet link to Model 2 Inputs. LBNL Utility-Scale Solar 2024 Ed., solar+storage PPA levels. https://emp.lbl.gov/utility-scale-solar
P_avg spot benchmark (this model) | 40 | $/MWh
Implied PPA premium over spot | 32 | $/MWh
Implied PPA premium (%) | 80% | frac | Premium reflects: (a) 15-20yr price certainty, (b) storage capacity value in a hybrid PPA, (c) RA attributes bundled with energy, (d) counterparty credit. Not a contradiction: a PPA above spot is the normal market structure.
Which price feeds Model 2 grid revenue?
Option A: keep $72 PPA (current v7) | 72 | $/MWh | Post-COD revenue assumes developer signs a contracted PPA. Consistent with how utility-scale projects are actually financed (lenders require contracted revenue). RECOMMENDED for base case.
Option B: merchant at P_avg | 40 | $/MWh | Post-COD revenue assumes merchant exposure to spot. Lower revenue, higher risk. Use as downside sensitivity: this is the 'no PPA available' case.
Option C: merchant at P_high (peak-shaped) | 89 | $/MWh | Only valid for dispatchable output (BESS discharge or geothermal) that can target evening peak. Not applicable to as-generated solar.
SEC 4: SOLAR CAPTURE RATE: material caveat for Solar+BESS configuration
SP15 solar capture rate (2024) | 30% | frac of ATC
Solar-weighted realized spot (P_avg × capture) | 12 | $/MWh | If a solar project sold merchant with no storage, its generation-weighted price would be roughly this. This is why Model 2 solar baseline IRR is weak and why BESS is structurally required: it shifts output from P_low hours toward P_high hours.

## M1_Notes
Model 1: Methodology Notes and Deviation from Original Stage 1 Specification
§1 What the proposal specified
Revised Proposal (May 2026), Stage 1: download CAISO OASIS day-ahead hourly LMP for 2023–2025 at TH_SP15/TH_NP15, bin each hour by concurrent system load percentile (bottom 20% / 30–70% / top 10%), compute load-weighted average LMP per bin, then overlay three carbon prices. Output: 9 benchmark prices.
§2 What was actually done, and why
Benchmarks are constructed from CAISO Department of Market Monitoring (DMM) published statistics: the 2024 and 2025 Annual Reports and the 2024 Q1–Q3 and 2025 Q4 quarterly reports: rather than from raw OASIS hourly downloads. Reasons: (a) DMM figures are official, load-weighted, and independently computed by CAISO's market monitor, which is a stronger provenance for a citable benchmark than a student-processed OASIS extract; (b) DMM publishes exactly the aggregates the framework needs (annual load-weighted DA mean, hourly load-weighted 15-min profile, GHG cost per MWh); (c) raw OASIS processing was deferred to preserve time for Models 2–4, which are the analytical core. The raw-OASIS path remains available as a robustness check (see §6).
§3 Binning: load percentile vs. hour-of-day proxy
The framework bins by system-load percentile. DMM does not publish load-percentile-binned prices, so this model uses hour-of-day regimes from DMM Q3 2024 Table 3.3 as the proxy. The framework's own descriptions: LOW = 'spring shoulder, high solar output hours'; HIGH = 'summer peak, evening ramp': are net-load concepts, and net load in CAISO is a function of hour-of-day far more than of gross load. Mid-day solar trough (HE10–13) is the empirical minimum in the DMM table; evening ramp (HE19–21) is the empirical maximum. The mapping is therefore faithful to the framework's economic intent, but it is a judgment call and should be stated as such in the paper.
§4 Known limitations
(a) Hourly profile is Q3 2024 only. Q3 has the deepest mid-day depression and the highest evening peak, so P_low is a conservative low and P_high is a conservative high relative to a full-year hourly average. P_avg is unaffected (annual figure). (b) 15-minute market hourly averages are used for the hourly profile because DMM publishes that table; DA and 15-min converge on average (DMM Q3 2024 §3.3: 'typically tend to converge on average due to convergence bidding'), so the substitution is minor. (c) PG&E and SCE DLAPs are blended equally; a project-specific run should weight by actual node (Salton Sea geothermal and Tehachapi wind are SP15/SCE-side; solar 'various'). (d) 2023 is excluded from P_avg because DMM documents 2023 as a gas-price anomaly (SoCal Citygate $5.12 vs $2.14/MMBtu); it is retained as an explicit high-price sensitivity.
§5 Carbon overlay
Adders are computed as incremental $/tCO2e × marginal emission rate. The emission rate (0.425 tCO2e/MWh) is not assumed: it is back-calculated from DMM's own statement of the GHG cost impact on 'a relatively efficient gas unit' in both 2024 ($16.19/MWh ÷ $38.09/t) and 2025 ($12.70/MWh ÷ $29.89/t), which agree to three decimals. This pins the framework's 0.4–0.6 range to its lower bound. Adders are incremental to the CA cap-and-trade cost already embedded in observed prices; the C0 scenario is the observed price, not a carbon-free counterfactual.
§6 Path to full OASIS replication (if time permits)
Use the gridstatus Python library: caiso.get_lmp(start='2023-01-01', end='2025-12-31', market='DAY_AHEAD_HOURLY', locations=['TH_SP15_GEN-APND','TH_NP15_GEN-APND']) and caiso.get_load(...). Merge on timestamp, compute load percentile per hour, groupby bin, load-weighted mean. Expected result: P_low and P_high move modestly toward P_avg (full-year vs Q3-only); P_avg unchanged. If replicated, report both and use OASIS as primary with DMM as the published-source cross-check.
§7 How Model 1 feeds the other models
→ Model 2 (DCF): the grid PPA price stays at $72/MWh (LBNL contracted hybrid PPA) for the base case; P_avg and P_high are sensitivity inputs for merchant-exposure cases. See M1_Scenarios SEC 3 for the reconciliation. → Model 3 (DC cost): Structure B 'PPA energy price' placeholder ($70) can be replaced by the Model 2 PPA link; P_avg is the VPPA settlement reference. → Model 4 (BTM pricing): P_avg + T&D stack (from Model 3 Structure B) forms the grid-alternative ceiling; the carbon scenarios shift the ceiling upward, widening the negotiation zone.

## Inputs
SPUR Preliminary Co-location Model v7: per-configuration tabs
Three yellow levers apply to ALL configurations simultaneously (keeps cross-config comparison consistent). Blue = editable. $ in millions.
SCENARIO LEVERS (GLOBAL)
Queue wait (mech. completion -> COD), years | 4 | Test 2/4/6/8 (LBNL Queued Up 2025: https://emp.lbl.gov/queues)
ITC rate | 30% | 0% = OBBBA Scenario D (zero credit under EITHER credit type); 30% = full rate w/ PWA
Credit type (1=ITC, 2=PTC) | 1 | Framework 2.3.5: run both; PTC uses full depreciable basis
SHARED PARAMETERS
PTC rate ($/MWh, full rate w/ PWA) | 15 | $0.015/kWh, 10-yr duration (Framework 2.3.4; inflation adjustment omitted)
BESS delivery loss (RTE approx.) | 1% | Annual approximation of round-trip losses
Debt interest rate | 5.5% | Framework 2.3.1: 5-7% range
Debt tenor (years) | 20 | Framework 2.3.1
Target DSCR (debt sizing) | 1.35 | Framework 2.7
Max leverage (% of total capital) | 55% | Framework 2.3.1: 50-55%; binds when DSCR-sized debt exceeds it (wind, geothermal)
Combined tax rate (fed + CA) | 29.84% | 21% federal + 8.84% CA
Tax equity pay rate (per $ benefit PV) | 80% | TE pays ~80c per $1 PV of ITC + PTC + MACRS shield
MACRS PV discount rate | 7% | Assumption
Grid hybrid PPA price ($/MWh) | 72 | LBNL Utility-Scale Solar (hybrid PPA levels): https://emp.lbl.gov/utility-scale-solar
BTM PPA price ($/MWh) | 60 | ~17% discount, within 10-20% industry range (Framework 4.3)
Asset management (% of revenue) | 1.5% | Framework 2.6
Construction years | 2 | Framework 2.1
Flip year (calendar) | 6 | Framework 2.8.2 default; 2.8.4 illustrative table uses 7: testable
Buyout at flip ($mm) | 1 | Nominal
NPV discount rate | 8% | Framework 2.9.3: 8% WACC
Developer cash share, pre-flip | 70% | Framework 2.8.2
Developer cash share, post-flip | 97.5% | Framework 2.8.2
BTM price source (1 = global B19, 2 = Model 4 per-config) | 2 | Set 1 to reproduce v7 results at flat $60. Set 2 to close the M4 to M2 loop.

## Configurations
Configuration library: each parameter feeds its configuration's tabs directly
Parameter | Solar+BESS 100MW | Wind+BESS 150MW | Geothermal+BESS 100MW | Source / note
Capacity (MW) | 100 | 150 | 100 | Solar/Geothermal: Framework 2.2.1. Wind: 150 MW scale variant (user-specified)
Capacity factor | 27.5% | 35% | 90% | Solar: CA midpoint. Wind: upper Tehachapi 30-35%. Geothermal: 90%+ Salton Sea/Imperial Valley (NREL ATB 2024: https://atb.nrel.gov/electricity/2024/technologies)
Annual degradation | 0.5% | 0.2% | 0% | Framework 2.5.2 (geothermal ~0%)
Availability | 98% | 96% | 95% | Framework 2.5.2
Electrical losses | 2.5% | 2.5% | 2.5% | Framework 2.5.2
Total CAPEX ($mm) | 197 | 321.4 | 568.25 | Solar: Framework 2.2.3. Wind: $1,350/kW x150 + BESS 75MW/300MWh @$1,250/kW + dev 4% + land + intercon. Geothermal: $5,000/kW x100 + BESS 25MW/50MWh + dev 4% + land + intercon (NREL ATB 2024 midpoints)
Qualified investment ($mm) | 180 | 296.25 | 531.25 | Generation + BESS only (Framework 2.2.4)
Microgrid CAPEX ($mm) | 12 | 18 | 12 | $120/kW midpoint of $50-150/kW x capacity
Fixed O&M, gen + BESS ($mm/yr) | 3 | 6.375 | 4.625 | Framework 2.6 midpoints per configuration
Land lease + insurance ($mm/yr) | 1.088 | 1.586 | 2.573 | $0.3mm land + 0.4% of CAPEX insurance
Microgrid O&M ($mm/yr) | 0.75 | 1.125 | 0.75 | $7.5/kW-yr x capacity
Operating life (years) | 25 | 25 | 30 | Framework 2.1: 25 yrs solar/wind, 30 yrs geothermal
BTM PPA price, effective ($/MWh) | 121.2562 | 116.3537 | 108.9349 | Switch on Inputs!B27. Source 2 pulls the Model 4 selected price (M4_Pricing SEC 3), which depends on the method selector and alpha lever there. Feeds the queue-wait revenue in each Coloc tab.
BTM PPA price at v7 default ($/MWh) | 60 | 60 | 60 | Reference: the flat $60 the v7 sweep tables in Results were generated with.
Notes: (1) Model finds ITC > PTC for all three configurations at these parameters: for geothermal this contradicts Framework 2.3.5's
expectation; sensitive to the omitted PTC inflation adjustment and the 7% discount on the PTC stream. (2) Geothermal faces no near-term
OBBBA deadline (phaseout from 2034), so the 0% ITC scenario is a stress test rather than a live policy risk for that configuration.

## Capitalization
Capitalization: debt = MIN(DSCR-sized, max leverage x capital); tax equity sized to ITC/PTC + MACRS shield
| Solar Base | Solar Coloc | Wind Base | Wind Coloc | Geo Base | Geo Coloc
Total capital required ($mm) | 197 | 209 | 321.4 | 339.4 | 568.25 | 580.25
First grid-year net energy (MWh) | 230179.95 | 230179.95 | 430466.4 | 430466.4 | 730255.5 | 730255.5
First grid-year revenue ($mm) | 16.573 | 16.573 | 30.9936 | 30.9936 | 52.5784 | 52.5784
First grid-year OPEX ($mm) | 4.3366 | 5.0866 | 8.4259 | 9.5509 | 7.9867 | 8.7367
First grid-year EBITDA ($mm) | 12.2364 | 11.4864 | 22.5677 | 21.4427 | 44.5917 | 43.8417
Max debt service @ DSCR ($mm/yr) | 9.064 | 8.5084 | 16.7168 | 15.8835 | 33.0309 | 32.4753
DSCR-sized debt ($mm) | 108.3179 | 101.6788 | 199.7721 | 189.8135 | 394.7319 | 388.0928
Senior debt after leverage cap ($mm) | 108.3179 | 101.6788 | 176.77 | 186.67 | 312.5375 | 319.1375
Actual debt service ($mm/yr) | 9.064 | 8.5084 | 14.792 | 15.6204 | 26.1529 | 26.7052
ITC amount ($mm) | 54 | 54 | 88.875 | 88.875 | 159.375 | 159.375
PTC start year (calendar) | 7 | 3 | 7 | 3 | 7 | 3
PTC stream PV ($mm) | 0 | 0 | 0 | 0 | 0 | 0
Depreciable basis ($mm) | 153 | 153 | 251.8125 | 251.8125 | 451.5625 | 451.5625
MACRS shield PV ($mm) | 37.9645 | 37.9645 | 62.4832 | 62.4832 | 112.048 | 112.048
Tax equity contribution ($mm) | 73.5716 | 73.5716 | 121.0866 | 121.0866 | 217.1384 | 217.1384
Developer equity ($mm) | 15.1105 | 33.7496 | 23.5434 | 31.6434 | 38.5741 | 43.9741
PTC start assumption: baseline is not placed in service while idle (PTC begins at COD); co-location BTM operation is assumed
to qualify as placed in service (PTC begins at mechanical completion). Open tax question: validate in practitioner interviews.
MACRS 5-yr schedule (Framework 2.3.3)
Year 1 | 20%
Year 2 | 32%
Year 3 | 19.2%
Year 4 | 11.52%
Year 5 | 11.52%
Year 6 | 5.76%

## SolarBase
SolarBase: annual cash flow waterfall ($mm)
Developer levered IRR: | 4.071% | Unlevered (project) IRR: | 0.9124% | NPV of dev cash @ discount rate ($mm): | -15.3966
Year | Phase | Op yr | Net energy (MWh) | Revenue | OPEX | EBITDA | Debt service | Distributable cash | Dev share | Dev cash flow | DSCR | Project CF (unlevered)
0 | Equity |  | 0 | 0 | 0 | 0 | 0 | 0 |  | -15.1105 |  | -197
1 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
2 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
3 | Queue wait | 0 | 230179.95 | 0 | 1.088 | -1.088 | 9.064 | -10.152 | 70% | -7.1064 | -0.12004 | -1.088
4 | Queue wait | 1 | 229029.0503 | 0 | 1.088 | -1.088 | 9.064 | -10.152 | 70% | -7.1064 | -0.12004 | -1.088
5 | Queue wait | 2 | 227883.905 | 0 | 1.088 | -1.088 | 9.064 | -10.152 | 70% | -7.1064 | -0.12004 | -1.088
6 | Queue wait | 3 | 226744.4855 | 0 | 1.088 | -1.088 | 9.064 | -10.152 | 70% | -8.1064 | -0.12004 | -1.088
7 | Grid ops | 4 | 225610.763 | 16.244 | 4.3317 | 11.9123 | 9.064 | 2.8483 | 97.5% | 2.7771 | 1.3142 | 11.9123
8 | Grid ops | 5 | 224482.7092 | 16.1628 | 4.3304 | 11.8323 | 9.064 | 2.7683 | 97.5% | 2.6991 | 1.3054 | 11.8323
9 | Grid ops | 6 | 223360.2957 | 16.0819 | 4.3292 | 11.7527 | 9.064 | 2.6887 | 97.5% | 2.6215 | 1.2966 | 11.7527
10 | Grid ops | 7 | 222243.4942 | 16.0015 | 4.328 | 11.6735 | 9.064 | 2.6095 | 97.5% | 2.5443 | 1.2879 | 11.6735
11 | Grid ops | 8 | 221132.2767 | 15.9215 | 4.3268 | 11.5947 | 9.064 | 2.5307 | 97.5% | 2.4675 | 1.2792 | 11.5947
12 | Grid ops | 9 | 220026.6154 | 15.8419 | 4.3256 | 11.5163 | 9.064 | 2.4523 | 97.5% | 2.391 | 1.2706 | 11.5163
13 | Grid ops | 10 | 218926.4823 | 15.7627 | 4.3244 | 11.4383 | 9.064 | 2.3743 | 97.5% | 2.3149 | 1.2619 | 11.4383
14 | Grid ops | 11 | 217831.8499 | 15.6839 | 4.3233 | 11.3606 | 9.064 | 2.2967 | 97.5% | 2.2392 | 1.2534 | 11.3606
15 | Grid ops | 12 | 216742.6906 | 15.6055 | 4.3221 | 11.2834 | 9.064 | 2.2194 | 97.5% | 2.1639 | 1.2449 | 11.2834
16 | Grid ops | 13 | 215658.9772 | 15.5274 | 4.3209 | 11.2065 | 9.064 | 2.1426 | 97.5% | 2.089 | 1.2364 | 11.2065
17 | Grid ops | 14 | 214580.6823 | 15.4498 | 4.3197 | 11.1301 | 9.064 | 2.0661 | 97.5% | 2.0144 | 1.2279 | 11.1301
18 | Grid ops | 15 | 213507.7789 | 15.3726 | 4.3186 | 11.054 | 9.064 | 1.99 | 97.5% | 1.9402 | 1.2196 | 11.054
19 | Grid ops | 16 | 212440.24 | 15.2957 | 4.3174 | 10.9783 | 9.064 | 1.9143 | 97.5% | 1.8664 | 1.2112 | 10.9783
20 | Grid ops | 17 | 211378.0388 | 15.2192 | 4.3163 | 10.9029 | 9.064 | 1.839 | 97.5% | 1.793 | 1.2029 | 10.9029
21 | Grid ops | 18 | 210321.1486 | 15.1431 | 4.3151 | 10.828 | 9.064 | 1.764 | 97.5% | 1.7199 | 1.1946 | 10.828
22 | Grid ops | 19 | 209269.5428 | 15.0674 | 4.314 | 10.7534 | 9.064 | 1.6894 | 97.5% | 1.6472 | 1.1864 | 10.7534
23 | Grid ops | 20 | 208223.1951 | 14.9921 | 4.3129 | 10.6792 | 0 | 10.6792 | 97.5% | 10.4122 |  | 10.6792
24 | Grid ops | 21 | 207182.0791 | 14.9171 | 4.3118 | 10.6054 | 0 | 10.6054 | 97.5% | 10.3402 |  | 10.6054
25 | Grid ops | 22 | 206146.1687 | 14.8425 | 4.3106 | 10.5319 | 0 | 10.5319 | 97.5% | 10.2686 |  | 10.5319
26 | Grid ops | 23 | 205115.4379 | 14.7683 | 4.3095 | 10.4588 | 0 | 10.4588 | 97.5% | 10.1973 |  | 10.4588
27 | Grid ops | 24 | 204089.8607 | 14.6945 | 4.3084 | 10.3861 | 0 | 10.3861 | 97.5% | 10.1264 |  | 10.3861
28 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
29 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
30 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
31 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
32 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0

## SolarColoc
SolarColoc: annual cash flow waterfall ($mm)
Developer levered IRR: | 11.79% | Unlevered (project) IRR: | 3.164% | NPV of dev cash @ discount rate ($mm): | 11.742
Year | Phase | Op yr | Net energy (MWh) | Revenue | OPEX | EBITDA | Debt service | Distributable cash | Dev share | Dev cash flow | DSCR | Project CF (unlevered)
0 | Equity |  | 0 | 0 | 0 | 0 | 0 | 0 |  | -33.7496 |  | -209
1 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
2 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
3 | Queue wait | 0 | 230179.95 | 27.6316 | 5.2525 | 22.3792 | 8.5084 | 13.8708 | 70% | 9.7095 | 2.6302 | 22.3792
4 | Queue wait | 1 | 229029.0503 | 27.4935 | 5.2504 | 22.2431 | 8.5084 | 13.7347 | 70% | 9.6143 | 2.6142 | 22.2431
5 | Queue wait | 2 | 227883.905 | 27.356 | 5.2483 | 22.1077 | 8.5084 | 13.5993 | 70% | 9.5195 | 2.5983 | 22.1077
6 | Queue wait | 3 | 226744.4855 | 27.2192 | 5.2463 | 21.973 | 8.5084 | 13.4645 | 70% | 8.4252 | 2.5825 | 21.973
7 | Grid ops | 4 | 225610.763 | 16.244 | 5.0817 | 11.1623 | 8.5084 | 2.6539 | 97.5% | 2.5876 | 1.3119 | 11.1623
8 | Grid ops | 5 | 224482.7092 | 16.1628 | 5.0804 | 11.0823 | 8.5084 | 2.5739 | 97.5% | 2.5095 | 1.3025 | 11.0823
9 | Grid ops | 6 | 223360.2957 | 16.0819 | 5.0792 | 11.0027 | 8.5084 | 2.4943 | 97.5% | 2.4319 | 1.2932 | 11.0027
10 | Grid ops | 7 | 222243.4942 | 16.0015 | 5.078 | 10.9235 | 8.5084 | 2.4151 | 97.5% | 2.3547 | 1.2838 | 10.9235
11 | Grid ops | 8 | 221132.2767 | 15.9215 | 5.0768 | 10.8447 | 8.5084 | 2.3363 | 97.5% | 2.2779 | 1.2746 | 10.8447
12 | Grid ops | 9 | 220026.6154 | 15.8419 | 5.0756 | 10.7663 | 8.5084 | 2.2579 | 97.5% | 2.2014 | 1.2654 | 10.7663
13 | Grid ops | 10 | 218926.4823 | 15.7627 | 5.0744 | 10.6883 | 8.5084 | 2.1798 | 97.5% | 2.1254 | 1.2562 | 10.6883
14 | Grid ops | 11 | 217831.8499 | 15.6839 | 5.0733 | 10.6106 | 8.5084 | 2.1022 | 97.5% | 2.0497 | 1.2471 | 10.6106
15 | Grid ops | 12 | 216742.6906 | 15.6055 | 5.0721 | 10.5334 | 8.5084 | 2.025 | 97.5% | 1.9744 | 1.238 | 10.5334
16 | Grid ops | 13 | 215658.9772 | 15.5274 | 5.0709 | 10.4565 | 8.5084 | 1.9481 | 97.5% | 1.8994 | 1.229 | 10.4565
17 | Grid ops | 14 | 214580.6823 | 15.4498 | 5.0697 | 10.3801 | 8.5084 | 1.8716 | 97.5% | 1.8249 | 1.22 | 10.3801
18 | Grid ops | 15 | 213507.7789 | 15.3726 | 5.0686 | 10.304 | 8.5084 | 1.7956 | 97.5% | 1.7507 | 1.211 | 10.304
19 | Grid ops | 16 | 212440.24 | 15.2957 | 5.0674 | 10.2283 | 8.5084 | 1.7198 | 97.5% | 1.6768 | 1.2021 | 10.2283
20 | Grid ops | 17 | 211378.0388 | 15.2192 | 5.0663 | 10.1529 | 8.5084 | 1.6445 | 97.5% | 1.6034 | 1.1933 | 10.1529
21 | Grid ops | 18 | 210321.1486 | 15.1431 | 5.0651 | 10.078 | 8.5084 | 1.5696 | 97.5% | 1.5303 | 1.1845 | 10.078
22 | Grid ops | 19 | 209269.5428 | 15.0674 | 5.064 | 10.0034 | 8.5084 | 1.495 | 97.5% | 1.4576 | 1.1757 | 10.0034
23 | Grid ops | 20 | 208223.1951 | 14.9921 | 5.0629 | 9.9292 | 0 | 9.9292 | 97.5% | 9.681 |  | 9.9292
24 | Grid ops | 21 | 207182.0791 | 14.9171 | 5.0618 | 9.8554 | 0 | 9.8554 | 97.5% | 9.609 |  | 9.8554
25 | Grid ops | 22 | 206146.1687 | 14.8425 | 5.0606 | 9.7819 | 0 | 9.7819 | 97.5% | 9.5373 |  | 9.7819
26 | Grid ops | 23 | 205115.4379 | 14.7683 | 5.0595 | 9.7088 | 0 | 9.7088 | 97.5% | 9.4661 |  | 9.7088
27 | Grid ops | 24 | 204089.8607 | 14.6945 | 5.0584 | 9.6361 | 0 | 9.6361 | 97.5% | 9.3952 |  | 9.6361
28 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
29 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
30 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
31 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
32 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0

## WindBase
WindBase: annual cash flow waterfall ($mm)
Developer levered IRR: | 7.647% | Unlevered (project) IRR: | 2.031% | NPV of dev cash @ discount rate ($mm): | -2.4701
Year | Phase | Op yr | Net energy (MWh) | Revenue | OPEX | EBITDA | Debt service | Distributable cash | Dev share | Dev cash flow | DSCR | Project CF (unlevered)
0 | Equity |  | 0 | 0 | 0 | 0 | 0 | 0 |  | -23.5434 |  | -321.4
1 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
2 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
3 | Queue wait | 0 | 430466.4 | 0 | 1.586 | -1.586 | 14.792 | -16.378 | 70% | -11.4646 | -0.10722 | -1.586
4 | Queue wait | 1 | 429605.4672 | 0 | 1.586 | -1.586 | 14.792 | -16.378 | 70% | -11.4646 | -0.10722 | -1.586
5 | Queue wait | 2 | 428746.2563 | 0 | 1.586 | -1.586 | 14.792 | -16.378 | 70% | -11.4646 | -0.10722 | -1.586
6 | Queue wait | 3 | 427888.7638 | 0 | 1.586 | -1.586 | 14.792 | -16.378 | 70% | -12.4646 | -0.10722 | -1.586
7 | Grid ops | 4 | 427032.9862 | 30.7464 | 8.4222 | 22.3242 | 14.792 | 7.5322 | 97.5% | 7.3439 | 1.5092 | 22.3242
8 | Grid ops | 5 | 426178.9203 | 30.6849 | 8.4213 | 22.2636 | 14.792 | 7.4716 | 97.5% | 7.2848 | 1.5051 | 22.2636
9 | Grid ops | 6 | 425326.5624 | 30.6235 | 8.4204 | 22.2032 | 14.792 | 7.4112 | 97.5% | 7.2259 | 1.501 | 22.2032
10 | Grid ops | 7 | 424475.9093 | 30.5623 | 8.4194 | 22.1428 | 14.792 | 7.3508 | 97.5% | 7.1671 | 1.4969 | 22.1428
11 | Grid ops | 8 | 423626.9575 | 30.5011 | 8.4185 | 22.0826 | 14.792 | 7.2906 | 97.5% | 7.1084 | 1.4929 | 22.0826
12 | Grid ops | 9 | 422779.7036 | 30.4401 | 8.4176 | 22.0225 | 14.792 | 7.2305 | 97.5% | 7.0498 | 1.4888 | 22.0225
13 | Grid ops | 10 | 421934.1441 | 30.3793 | 8.4167 | 21.9626 | 14.792 | 7.1706 | 97.5% | 6.9913 | 1.4848 | 21.9626
14 | Grid ops | 11 | 421090.2759 | 30.3185 | 8.4158 | 21.9027 | 14.792 | 7.1107 | 97.5% | 6.933 | 1.4807 | 21.9027
15 | Grid ops | 12 | 420248.0953 | 30.2579 | 8.4149 | 21.843 | 14.792 | 7.051 | 97.5% | 6.8747 | 1.4767 | 21.843
16 | Grid ops | 13 | 419407.5991 | 30.1973 | 8.414 | 21.7834 | 14.792 | 6.9914 | 97.5% | 6.8166 | 1.4726 | 21.7834
17 | Grid ops | 14 | 418568.7839 | 30.137 | 8.4131 | 21.7239 | 14.792 | 6.9319 | 97.5% | 6.7586 | 1.4686 | 21.7239
18 | Grid ops | 15 | 417731.6464 | 30.0767 | 8.4122 | 21.6645 | 14.792 | 6.8725 | 97.5% | 6.7007 | 1.4646 | 21.6645
19 | Grid ops | 16 | 416896.1831 | 30.0165 | 8.4112 | 21.6053 | 14.792 | 6.8133 | 97.5% | 6.643 | 1.4606 | 21.6053
20 | Grid ops | 17 | 416062.3907 | 29.9565 | 8.4103 | 21.5461 | 14.792 | 6.7541 | 97.5% | 6.5853 | 1.4566 | 21.5461
21 | Grid ops | 18 | 415230.2659 | 29.8966 | 8.4094 | 21.4871 | 14.792 | 6.6951 | 97.5% | 6.5278 | 1.4526 | 21.4871
22 | Grid ops | 19 | 414399.8054 | 29.8368 | 8.4086 | 21.4282 | 14.792 | 6.6362 | 97.5% | 6.4703 | 1.4486 | 21.4282
23 | Grid ops | 20 | 413571.0058 | 29.7771 | 8.4077 | 21.3695 | 0 | 21.3695 | 97.5% | 20.8352 |  | 21.3695
24 | Grid ops | 21 | 412743.8638 | 29.7176 | 8.4068 | 21.3108 | 0 | 21.3108 | 97.5% | 20.778 |  | 21.3108
25 | Grid ops | 22 | 411918.376 | 29.6581 | 8.4059 | 21.2523 | 0 | 21.2523 | 97.5% | 20.7209 |  | 21.2523
26 | Grid ops | 23 | 411094.5393 | 29.5988 | 8.405 | 21.1938 | 0 | 21.1938 | 97.5% | 20.664 |  | 21.1938
27 | Grid ops | 24 | 410272.3502 | 29.5396 | 8.4041 | 21.1355 | 0 | 21.1355 | 97.5% | 20.6071 |  | 21.1355
28 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
29 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
30 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
31 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
32 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0

## WindColoc
WindColoc: annual cash flow waterfall ($mm)
Developer levered IRR: | 24.44% | Unlevered (project) IRR: | 4.604% | NPV of dev cash @ discount rate ($mm): | 58.258
Year | Phase | Op yr | Net energy (MWh) | Revenue | OPEX | EBITDA | Debt service | Distributable cash | Dev share | Dev cash flow | DSCR | Project CF (unlevered)
0 | Equity |  | 0 | 0 | 0 | 0 | 0 | 0 |  | -31.6434 |  | -339.4
1 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
2 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
3 | Queue wait | 0 | 430466.4 | 49.5855 | 9.8298 | 39.7557 | 15.6204 | 24.1353 | 70% | 16.8947 | 2.5451 | 39.7557
4 | Queue wait | 1 | 429605.4672 | 49.4863 | 9.8283 | 39.658 | 15.6204 | 24.0376 | 70% | 16.8263 | 2.5389 | 39.658
5 | Queue wait | 2 | 428746.2563 | 49.3874 | 9.8268 | 39.5606 | 15.6204 | 23.9401 | 70% | 16.7581 | 2.5326 | 39.5606
6 | Queue wait | 3 | 427888.7638 | 49.2886 | 9.8253 | 39.4633 | 15.6204 | 23.8428 | 70% | 15.69 | 2.5264 | 39.4633
7 | Grid ops | 4 | 427032.9862 | 30.7464 | 9.5472 | 21.1992 | 15.6204 | 5.5788 | 97.5% | 5.4393 | 1.3571 | 21.1992
8 | Grid ops | 5 | 426178.9203 | 30.6849 | 9.5463 | 21.1386 | 15.6204 | 5.5182 | 97.5% | 5.3802 | 1.3533 | 21.1386
9 | Grid ops | 6 | 425326.5624 | 30.6235 | 9.5454 | 21.0782 | 15.6204 | 5.4577 | 97.5% | 5.3213 | 1.3494 | 21.0782
10 | Grid ops | 7 | 424475.9093 | 30.5623 | 9.5444 | 21.0178 | 15.6204 | 5.3974 | 97.5% | 5.2625 | 1.3455 | 21.0178
11 | Grid ops | 8 | 423626.9575 | 30.5011 | 9.5435 | 20.9576 | 15.6204 | 5.3372 | 97.5% | 5.2038 | 1.3417 | 20.9576
12 | Grid ops | 9 | 422779.7036 | 30.4401 | 9.5426 | 20.8975 | 15.6204 | 5.2771 | 97.5% | 5.1452 | 1.3378 | 20.8975
13 | Grid ops | 10 | 421934.1441 | 30.3793 | 9.5417 | 20.8376 | 15.6204 | 5.2171 | 97.5% | 5.0867 | 1.334 | 20.8376
14 | Grid ops | 11 | 421090.2759 | 30.3185 | 9.5408 | 20.7777 | 15.6204 | 5.1573 | 97.5% | 5.0284 | 1.3302 | 20.7777
15 | Grid ops | 12 | 420248.0953 | 30.2579 | 9.5399 | 20.718 | 15.6204 | 5.0976 | 97.5% | 4.9701 | 1.3263 | 20.718
16 | Grid ops | 13 | 419407.5991 | 30.1973 | 9.539 | 20.6584 | 15.6204 | 5.038 | 97.5% | 4.912 | 1.3225 | 20.6584
17 | Grid ops | 14 | 418568.7839 | 30.137 | 9.5381 | 20.5989 | 15.6204 | 4.9785 | 97.5% | 4.854 | 1.3187 | 20.5989
18 | Grid ops | 15 | 417731.6464 | 30.0767 | 9.5372 | 20.5395 | 15.6204 | 4.9191 | 97.5% | 4.7961 | 1.3149 | 20.5395
19 | Grid ops | 16 | 416896.1831 | 30.0165 | 9.5362 | 20.4803 | 15.6204 | 4.8599 | 97.5% | 4.7384 | 1.3111 | 20.4803
20 | Grid ops | 17 | 416062.3907 | 29.9565 | 9.5353 | 20.4211 | 15.6204 | 4.8007 | 97.5% | 4.6807 | 1.3073 | 20.4211
21 | Grid ops | 18 | 415230.2659 | 29.8966 | 9.5344 | 20.3621 | 15.6204 | 4.7417 | 97.5% | 4.6232 | 1.3036 | 20.3621
22 | Grid ops | 19 | 414399.8054 | 29.8368 | 9.5336 | 20.3032 | 15.6204 | 4.6828 | 97.5% | 4.5657 | 1.2998 | 20.3032
23 | Grid ops | 20 | 413571.0058 | 29.7771 | 9.5327 | 20.2445 | 0 | 20.2445 | 97.5% | 19.7383 |  | 20.2445
24 | Grid ops | 21 | 412743.8638 | 29.7176 | 9.5318 | 20.1858 | 0 | 20.1858 | 97.5% | 19.6811 |  | 20.1858
25 | Grid ops | 22 | 411918.376 | 29.6581 | 9.5309 | 20.1273 | 0 | 20.1273 | 97.5% | 19.6241 |  | 20.1273
26 | Grid ops | 23 | 411094.5393 | 29.5988 | 9.53 | 20.0688 | 0 | 20.0688 | 97.5% | 19.5671 |  | 20.0688
27 | Grid ops | 24 | 410272.3502 | 29.5396 | 9.5291 | 20.0105 | 0 | 20.0105 | 97.5% | 19.5103 |  | 20.0105
28 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
29 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
30 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
31 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0
32 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5% | 0 |  | 0

## GeoBase
GeoBase: annual cash flow waterfall ($mm)
Developer levered IRR: | 11.61% | Unlevered (project) IRR: | 3.856% | NPV of dev cash @ discount rate ($mm): | 57.6358
Year | Phase | Op yr | Net energy (MWh) | Revenue | OPEX | EBITDA | Debt service | Distributable cash | Dev share | Dev cash flow | DSCR | Project CF (unlevered)
0 | Equity |  | 0 | 0 | 0 | 0 | 0 | 0 |  | -38.5741 |  | -568.25
1 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
2 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
3 | Queue wait | 0 | 730255.5 | 0 | 2.573 | -2.573 | 26.1529 | -28.7259 | 70% | -20.1082 | -0.098383 | -2.573
4 | Queue wait | 1 | 730255.5 | 0 | 2.573 | -2.573 | 26.1529 | -28.7259 | 70% | -20.1082 | -0.098383 | -2.573
5 | Queue wait | 2 | 730255.5 | 0 | 2.573 | -2.573 | 26.1529 | -28.7259 | 70% | -20.1082 | -0.098383 | -2.573
6 | Queue wait | 3 | 730255.5 | 0 | 2.573 | -2.573 | 26.1529 | -28.7259 | 70% | -21.1082 | -0.098383 | -2.573
7 | Grid ops | 4 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
8 | Grid ops | 5 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
9 | Grid ops | 6 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
10 | Grid ops | 7 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
11 | Grid ops | 8 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
12 | Grid ops | 9 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
13 | Grid ops | 10 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
14 | Grid ops | 11 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
15 | Grid ops | 12 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
16 | Grid ops | 13 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
17 | Grid ops | 14 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
18 | Grid ops | 15 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
19 | Grid ops | 16 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
20 | Grid ops | 17 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
21 | Grid ops | 18 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
22 | Grid ops | 19 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 26.1529 | 18.4388 | 97.5% | 17.9778 | 1.705 | 44.5917
23 | Grid ops | 20 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
24 | Grid ops | 21 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
25 | Grid ops | 22 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
26 | Grid ops | 23 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
27 | Grid ops | 24 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
28 | Grid ops | 25 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
29 | Grid ops | 26 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
30 | Grid ops | 27 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
31 | Grid ops | 28 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917
32 | Grid ops | 29 | 730255.5 | 52.5784 | 7.9867 | 44.5917 | 0 | 44.5917 | 97.5% | 43.4769 |  | 44.5917

## GeoColoc
GeoColoc: annual cash flow waterfall ($mm)
Developer levered IRR: | 33.08% | Unlevered (project) IRR: | 6.537% | NPV of dev cash @ discount rate ($mm): | 186.6642
Year | Phase | Op yr | Net energy (MWh) | Revenue | OPEX | EBITDA | Debt service | Distributable cash | Dev share | Dev cash flow | DSCR | Project CF (unlevered)
0 | Equity |  | 0 | 0 | 0 | 0 | 0 | 0 |  | -43.9741 |  | -580.25
1 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
2 | Construction |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
3 | Queue wait | 0 | 730255.5 | 78.7548 | 9.1293 | 69.6255 | 26.7052 | 42.9203 | 70% | 30.0442 | 2.6072 | 69.6255
4 | Queue wait | 1 | 730255.5 | 78.7548 | 9.1293 | 69.6255 | 26.7052 | 42.9203 | 70% | 30.0442 | 2.6072 | 69.6255
5 | Queue wait | 2 | 730255.5 | 78.7548 | 9.1293 | 69.6255 | 26.7052 | 42.9203 | 70% | 30.0442 | 2.6072 | 69.6255
6 | Queue wait | 3 | 730255.5 | 78.7548 | 9.1293 | 69.6255 | 26.7052 | 42.9203 | 70% | 29.0442 | 2.6072 | 69.6255
7 | Grid ops | 4 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
8 | Grid ops | 5 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
9 | Grid ops | 6 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
10 | Grid ops | 7 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
11 | Grid ops | 8 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
12 | Grid ops | 9 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
13 | Grid ops | 10 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
14 | Grid ops | 11 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
15 | Grid ops | 12 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
16 | Grid ops | 13 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
17 | Grid ops | 14 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
18 | Grid ops | 15 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
19 | Grid ops | 16 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
20 | Grid ops | 17 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
21 | Grid ops | 18 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
22 | Grid ops | 19 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 26.7052 | 17.1365 | 97.5% | 16.7081 | 1.6417 | 43.8417
23 | Grid ops | 20 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
24 | Grid ops | 21 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
25 | Grid ops | 22 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
26 | Grid ops | 23 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
27 | Grid ops | 24 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
28 | Grid ops | 25 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
29 | Grid ops | 26 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
30 | Grid ops | 27 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
31 | Grid ops | 28 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417
32 | Grid ops | 29 | 730255.5 | 52.5784 | 8.7367 | 43.8417 | 0 | 43.8417 | 97.5% | 42.7457 |  | 43.8417

## Results
Results: all three configurations side by side (live; global levers on Inputs)
| Solar+BESS 100MW | Wind+BESS 150MW | Geothermal+BESS 100MW
Baseline developer levered IRR | 4.071% | 7.647% | 11.61%
Co-location developer levered IRR | 11.79% | 24.44% | 33.08%
Delta IRR (co-location - baseline), pp | 7.723 | 16.796 | 21.4681
Baseline unlevered (project) IRR | 0.9124% | 2.031% | 3.856%
Co-location unlevered (project) IRR | 3.164% | 4.604% | 6.537%
Baseline NPV of dev cash ($mm) | -15.3966 | -2.4701 | 57.6358
Co-location NPV of dev cash ($mm) | 11.742 | 58.258 | 186.6642
VALUE BRIDGE: dollar impact of co-location over the queue-wait window (live)
Queue-wait revenue uplift, total ($mm) | 109.7004 | 197.7478 | 315.0192
Queue-wait revenue uplift, per year ($mm/yr) | 27.4251 | 49.4369 | 78.7548
Queue-wait EBITDA uplift, total ($mm) | 93.0549 | 164.7816 | 288.7939
Queue-wait developer cash uplift, total ($mm) | 66.694 | 113.0275 | 200.6093
vs. Microgrid CAPEX ($mm) | 12 | 18 | 12
vs. Incremental developer equity ($mm) | 18.6391 | 8.1 | 5.4
Delta NPV of developer cash ($mm) | 27.1385 | 60.7282 | 129.0284
Scenario sweep: Solar+BESS 100MW (ITC pathway, flip yr 6; reproduce via Inputs levers)
ITC | Queue (yrs) | Baseline IRR | Co-location IRR | Delta (pp)
30% | 2 | 6.98% | 4.93% | -2.05
30% | 4 | 4.07% | 4.41% | 0.34
30% | 6 | 1.4% | 3.77% | 2.38
30% | 8 | -0.61% | 3.21% | 3.82
0% | 2 | -0.84% | -1.14% | -0.31
0% | 4 | -2.01% | -1.41% | 0.6
0% | 6 | -3.05% | -1.67% | 1.38
0% | 8 | -4.05% | -1.93% | 2.11
Scenario sweep: Wind+BESS 150MW (ITC pathway, flip yr 6; reproduce via Inputs levers)
ITC | Queue (yrs) | Baseline IRR | Co-location IRR | Delta (pp)
30% | 2 | 11.33% | 11.07% | -0.26
30% | 4 | 7.65% | 10.06% | 2.41
30% | 6 | 4.43% | 8.98% | 4.55
30% | 8 | 2.1% | 8.11% | 6.01
0% | 2 | 1.49% | 1.16% | -0.33
0% | 4 | 0.15% | 0.82% | 0.68
0% | 6 | -1.02% | 0.5% | 1.52
0% | 8 | -2.09% | 0.19% | 2.28
Scenario sweep: Geothermal+BESS 100MW (ITC pathway, flip yr 6; reproduce via Inputs levers)
ITC | Queue (yrs) | Baseline IRR | Co-location IRR | Delta (pp)
30% | 2 | 15.72% | 20.06% | 4.35
30% | 4 | 11.61% | 18.82% | 7.21
30% | 6 | 8.32% | 17.64% | 9.32
30% | 8 | 6.12% | 16.79% | 10.67
0% | 2 | 4.69% | 5.57% | 0.87
0% | 4 | 3.42% | 5.26% | 1.84
0% | 6 | 2.38% | 5% | 2.61
0% | 8 | 1.49% | 4.76% | 3.27
Takeaways: Q* ~3.5 yrs (solar), ~2.2 yrs (wind), <2 yrs (geothermal, 30% ITC). Delta IRR rises with capacity factor: geothermal shows the
LARGEST improvement (+4.4 to +10.7pp), contradicting H1's expectation of the smallest: the delta is driven by energy monetized per queue
year, not by baseline IRR level. ITC beats PTC for all three configs at these parameters (PTC inflation adjustment omitted: caveat).
M4 LOOP CLOSURE: co-location IRR at flat $60 (v7 sweep) vs at Model 4 per-config BTM
Effective BTM price now in use ($/MWh) | 121.2562 | 116.3537 | 108.9349
Co-location levered IRR at flat $60 (from v7 sweep, 4yr/30%) | 4.41% | 10.06% | 18.82%
Co-location levered IRR, live at effective BTM | 11.79% | 24.44% | 33.08%
IRR change from closing the loop, pp | 7.3843 | 14.3832 | 14.262
Comparison valid only when Inputs!B5 = 4 and B6 = 0.30 (the sweep cell used). Baseline IRR is unaffected by BTM price.

## M3_Inputs
Model 3 - Data Center Electricity Cost Model - INPUTS
Blue = hardcoded input. Yellow = PLACEHOLDER pending sourced data. Column D = source.
SEC 1: DATA CENTER LOAD
DC nameplate load | 100 | MW | Scenario setting (user; central case of 50/100/200 MW matrix)
DC load factor | 90% | frac | PLACEHOLDER - AI DC annualized utilization; to be sourced (lit. / Chien interview). Typical claim 85-95%.
Hours per year | 8760 | hrs | Constant
Annual DC demand | 788400 | MWh/yr | Calc: nameplate x LF x 8760
SEC 2: GENERATION SUPPLY (from Model 2 configs)
Solar net capacity factor | 26% | frac | PLACEHOLDER - Model 2 SolarBase net of degradation/availability/losses (gross CF 25-30%, NREL ATB 2024, https://atb.nrel.gov/electricity/2024/technologies)
Wind net capacity factor | 33% | frac | PLACEHOLDER - Model 2 WindBase net (gross 30-35%, NREL ATB 2024)
Geothermal net capacity factor | 87% | frac | PLACEHOLDER - Model 2 GeoBase net (gross 90%+, NREL ATB 2024)
Solar capacity | 100 | MW | Model 2 configuration
Wind capacity | 150 | MW | Model 2 configuration
Geothermal capacity | 100 | MW | Model 2 configuration
BESS round-trip efficiency | 87.5% | frac | Framework Sec 2.5.3 (85-90%); applied to shifted energy share - simplified: coverage treated as energy-balance bound, hourly dispatch pending
SEC 3: PRICES - SOURCED
CAISO HV Transmission Access Charge (TAC) | 15.5751 | $/MWh | CAISO, High Voltage Access Charge Rates effective Jan 1 2026, https://www.caiso.com/documents/high-voltage-access-charge-rates-effective-jan-01-2026.pdf
RA capacity price (system, wtd avg) | 25.19 | $/kW-mo | CPUC, 2025 LCR-RCM calculation (Q1-Q4 2024 contracts, 2025-26 delivery), https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/energy-division/documents/resource-adequacy-homepage/resource-adequacy-compliance-materials/lcr-rcm-2025.pdf
Planning reserve margin (PRM) | 18% | frac | CPUC D.25-06-048 (June 2025), Slice-of-Day framework, https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/energy-division/documents/resource-adequacy-homepage/oga-fact-sheet-on-track-3-decision-final.pdf
Utility bundled all-in rate (Structure A) | 236.91 | $/MWh | PG&E Schedule B-20 Primary, total electricity cost $0.23691/kWh, rates as of Mar 1 2026, PG&E-3CE Joint Rate Comparison, https://www.pge.com/assets/pge/docs/account/alternate-energy-providers/3ce-rcc.pdf. Note: transmission-voltage (B-20 T) would be somewhat lower; treat as upper reference.
EIA-861 CA industrial avg (cross-check) | 215.3 | $/MWh | EIA-861 2024, California industrial average retail price (prior extraction; re-verify at https://www.eia.gov/electricity/data/eia861/)
Non-bypassable charges (NBC: PCIA/PPP/ND/wildfire) | 23 | $/MWh | PLACEHOLDER - anchored to PG&E PCIA/FF line ~$0.023/kWh in PG&E joint rate comparisons (see B-20 rows, same PG&E PDFs); decompose properly from PG&E/SCE tariff sheets
SEC 4: PRICES - PLACEHOLDERS (pending Model 1 / Model 4)
Grid PPA energy price (Structure B) | 70 | $/MWh | PLACEHOLDER - market comparable needed (LevelTen CAISO index or similar); do NOT reuse project LCOE (circularity)
BTM PPA price (Structure C) | 62 | $/MWh | PLACEHOLDER - Model 4 output pending; currently midpoint assumption from Model 2
Ancillary services + CAISO GMC | 1.5 | $/MWh | PLACEHOLDER - CAISO GMC ~$0.4-0.5 + AS; source from CAISO market charges schedule
Scheduling coordinator fee | 0.5 | $/MWh | PLACEHOLDER
Shaping / imbalance cost | 7 | $/MWh | PLACEHOLDER - as-generated renewable vs flat load mismatch; source from hourly dispatch model when built
Microgrid service fee (paid by DC) | 3.5 | $/MWh | Framework Sec 3.2 range $2-5/MWh. ALLOCATION ASSUMPTION: microgrid CAPEX sits in Model 2 project CAPEX; DC pays service fee only - no double count
Backup power cost (diesel, Phase 1) | 300 | $/MWh | PLACEHOLDER - CA diesel gen fuel+O&M+permits; source needed (e.g., Lazard LCOE+ gas peaking as proxy, CARB permit constraints)
Standby charge (Phase 2, grid backup) | 5 | $/MWh | PLACEHOLDER - CPUC standby/departing-load tariff (e.g., PG&E Schedule S); convert $/kW-mo to $/MWh once sourced

## M3_Coverage
Energy-Balance Coverage by Configuration
Coverage = min(1, annual net generation / annual DC demand). Energy-balance upper bound: BESS shifts timing but cannot create energy. Hourly dispatch (pending) will only lower these.
| Solar+BESS | Wind+BESS | Geo+BESS
Capacity (MW) | 100 | 150 | 100
Net capacity factor | 26% | 33% | 87%
Annual net generation (MWh) | 227760 | 433620 | 762120
Annual DC demand (MWh) | 788400 | 788400 | 788400
Coverage ratio (capped at 100%) | 28.89% | 55% | 96.67%
Uncovered share (backup/grid) | 71.11% | 45% | 3.333%

## M3_StructA_B
Structure A: Utility Tariff (bundled, all-in)
All-in delivered cost ($/MWh) | 236.91 | PG&E B-20 Primary, Mar 2026. Upper reference; transmission voltage would be lower.
Cross-check: EIA-861 CA industrial avg | 215.3
Structure B: Sleeved Grid PPA (all-in delivered)
VPPA treated as sensitivity (see note row 20). Sleeved = physical delivery via grid at transmission voltage.
PPA energy price | 70 | Placeholder pending market comp
CAISO TAC (HV) | 15.5751 | Sourced - CAISO Jan 2026
Non-bypassable charges | 23 | Placeholder range
Resource Adequacy | 45.2423 | Calc: nameplate kW x (1+PRM) x $/kW-mo x 12 / annual MWh. Price and PRM sourced.
Ancillary + GMC | 1.5 | Placeholder
Scheduling coordinator | 0.5 | Placeholder
Shaping / imbalance | 7 | Placeholder
Structure B all-in ($/MWh) | 162.8174
KEY FINDING
RA capacity cost alone adds ~$45/MWh to a flat 100 MW load. Structure B all-in far exceeds the framework's $60-90/MWh estimate, resolving the Model 3 internal inconsistency in the direction of a WIDER negotiation zone.
VPPA sensitivity: VPPA cost = Structure A retail cost + (PPA price - hub LMP settlement). Requires Model 1 LMP; deferred.

## M3_StructC
Structure C: BTM Co-location (all-in $/MWh to the DC)
Phase 1 = islanded (queue wait): backup fills uncovered share. Phase 2 = grid-connected: grid supply fills uncovered share.
| Solar+BESS | Wind+BESS | Geo+BESS
Coverage ratio | 28.89% | 55% | 96.67%
PHASE 1 (islanded, queue-wait window)
BTM energy component | 17.9111 | 34.1 | 59.9333
Backup component (uncovered x diesel) | 213.3333 | 135 | 10
Microgrid service fee | 3.5 | 3.5 | 3.5
Phase 1 all-in ($/MWh) | 234.7444 | 172.6 | 73.4333
PHASE 2 (grid-connected, post-COD)
BTM energy component | 17.9111 | 34.1 | 59.9333
Grid supplemental (uncovered x [PPA+TAC+NBC]) | 77.209 | 48.8588 | 3.6192
Standby charge | 5 | 5 | 5
Microgrid service fee | 3.5 | 3.5 | 3.5
Phase 2 all-in ($/MWh) | 103.6201 | 91.4588 | 72.0525
Note: Phase 2 grid supplemental assumes RA embedded in supplemental supply price is NOT separately charged (conservative low); alternative adds pro-rata RA - test in sensitivity.

## M3_Results
Model 3 Results - Effective Delivered Cost and H2 Test
| Solar+BESS | Wind+BESS | Geo+BESS
Structure A - utility tariff ($/MWh) | 236.91 | 236.91 | 236.91
Structure B - sleeved grid PPA all-in ($/MWh) | 162.8174 | 162.8174 | 162.8174
Structure C - Phase 1 islanded ($/MWh) | 234.7444 | 172.6 | 73.4333
Structure C - Phase 2 grid-connected ($/MWh) | 103.6201 | 91.4588 | 72.0525
H2 TEST - dual denominator
Savings, P1 vs B all-in: (B-C1)/B | -44.18% | -6.008% | 54.9%
Savings, P2 vs B all-in: (B-C2)/B | 36.36% | 43.83% | 55.75%
Savings, P1 vs B PPA price only | -235.3% | -146.6% | -4.905%
Savings, P2 vs B PPA price only | -48.03% | -30.66% | -2.932%
H2 (20-35%) met on all-in basis, Phase 1? | NO | NO | YES
READING
The vs-PPA-price-only rows will show negative 'savings' for low-coverage configs (solar) because backup cost dominates - this is why the all-in denominator is the meaningful H2 test.

## M4_LCOE
Model 4: Levelized Cost of Energy (price FLOOR for BTM negotiation)
LCOE = [CAPEX + PV(OPEX)] / PV(Energy). Green = linked from Configurations / Capitalization (Model 2). Yellow = headline floor. Closed-form annuity formulas; all live.
SEC 1: SHARED PARAMETERS
Discount rate (WACC proxy) | 8% | frac | Linked to Model 2 NPV discount rate (8%). Framework 2.4: WACC ~7-9%.
Hours per year | 8760 | hrs
SEC 2: LCOE BUILD-UP BY CONFIGURATION
| Solar+BESS 100MW | Wind+BESS 150MW | Geo+BESS 100MW | Source / formula
Capacity (MW) | 100 | 150 | 100 | Configurations R4
Capacity factor | 27.5% | 35% | 90% | Configurations R5
Availability | 98% | 96% | 95% | Configurations R7
Electrical losses | 2.5% | 2.5% | 2.5% | Configurations R8
Annual degradation | 0.5% | 0.2% | 0% | Configurations R6
Operating life (yrs) | 25 | 25 | 30 | Configurations R15
Year-1 net energy (MWh) | 230179.95 | 430466.4 | 730255.5 | Formula: mw × CF × 8760 × avail × (1−loss)
Total CAPEX, baseline ($mm) | 197 | 321.4 | 568.25 | Configurations R9: excludes microgrid
Microgrid CAPEX ($mm) | 12 | 18 | 12 | Configurations R11
Total CAPEX, co-location ($mm) | 209 | 339.4 | 580.25 | Formula: baseline + microgrid
Fixed O&M gen+BESS ($mm/yr) | 3 | 6.375 | 4.625 | Configurations R12
Land + insurance ($mm/yr) | 1.088 | 1.586 | 2.573 | Configurations R13
Microgrid O&M ($mm/yr) | 0.75 | 1.125 | 0.75 | Configurations R14
Annual OPEX, baseline ($mm/yr) | 4.088 | 7.961 | 7.198 | Formula: o&m + land/ins (no microgrid)
Annual OPEX, co-location ($mm/yr) | 4.838 | 9.086 | 7.948 | Formula: o&m + land/ins + microgrid o&m
ITC amount @ lever rate ($mm) | 54 | 88.875 | 159.375 | Capitalization R13 (base col)
Tax equity contribution ($mm) | 73.5716 | 121.0866 | 217.1384 | Capitalization R18 (base col): what TE actually pays for the credits
SEC 3: PRESENT-VALUE FACTORS
PV annuity factor for level OPEX | 10.6748 | 10.6748 | 11.2578 | Formula: [1 − (1+r)^−N] / r
Degradation-adjusted growth q = (1−d)/(1+r) | 0.9213 | 0.92407 | 0.92593
PV energy factor (yrs of Y1-equivalent) | 10.1979 | 10.4803 | 11.2578 | Formula: q(1−q^N)/(1−q); geometric series of degrading output discounted at r)
PV of lifetime energy (MWh) | 2347359.2835 | 4511435.9389 | 8221058.2041
SEC 4: LCOE OUTPUTS ($/MWh)
| Solar+BESS 100MW | Wind+BESS 150MW | Geo+BESS 100MW | Interpretation
LCOE: baseline, no credit (gross) | 102.5146 | 90.0782 | 78.9781 | Full project cost with no tax-credit offset. OBBBA Scenario D floor.
LCOE: co-location, no credit (gross) | 111.0374 | 96.73 | 81.4648 | Adds microgrid CAPEX + O&M. This is the physical floor for a BTM sale with zero credits.
LCOE: baseline, net of tax equity | 71.1723 | 63.2382 | 52.5656 | CAPEX reduced by tax-equity contribution (Capitalization R18). Developer's effective cost floor at current ITC lever.
LCOE: co-location, net of tax equity | 79.6951 | 69.89 | 55.0523 | BASE-CASE FLOOR. Co-location CAPEX net of tax equity. Feeds M4_Bounds.
Cross-check vs NREL ATB 2024 generation-only LCOE ranges
NREL ATB 2024 (moderate, R&D+Market) | Solar PV $24–42 | Wind $25–50 | Geothermal $55–80 | Framework Sec 2.4 table. Model values are HIGHER because they include BESS ($113–159 LCOS), microgrid, land, interconnection: ATB is bare generation. https://atb.nrel.gov/electricity/2024/technologies

## M4_Bounds
Model 4: Price Floor, Ceiling, and Negotiation Zone
Floor = developer's LCOE (M4_LCOE). Ceiling = data center's grid alternative (M3 Structure B). Zone = Ceiling − Floor. Framework Sec 4.2: 'If LCOE > Grid PPA Cost, co-location is not viable at any price.'
SEC 1: CEILING: data center's grid alternative (config-independent)
Ceiling A: Structure B all-in delivered | 162.8174 | $/MWh | PRIMARY CEILING per framework Sec 4.2. Sleeved PPA energy + TAC + NBC + RA + AS + SC + shaping. What the DC actually avoids by going BTM.
Ceiling B: energy-only market PPA | 72 | $/MWh | LBNL hybrid PPA ($72). Reference point for the 'industry 10-20% discount' convention (framework 4.3). NOT the true ceiling: DC also avoids T&D.
Ceiling C: spot + wires (Phase-2 supplemental) | 78.5751 | $/MWh | P_avg (M1) + CAISO TAC + NBC. Lower-bound ceiling: merchant grid supply with no RA. Used in M3 Phase 2 supplemental.
T&D + capacity savings pool (A − B) | 90.8174 | $/MWh | The non-energy charges avoided by BTM. Framework 4.3: 'allocating the T&D savings roughly 50/50 between the parties'.
SEC 2: FLOOR & ZONE BY CONFIGURATION
| Solar+BESS | Wind+BESS | Geo+BESS | Note
Floor: LCOE gross (no credit) | 111.0374 | 96.73 | 81.4648 | OBBBA Scenario D / FEOC-fail floor
Floor: LCOE net of tax equity (BASE) | 79.6951 | 69.89 | 55.0523 | Base-case floor at current ITC lever (Inputs!B6)
Zone vs Ceiling A (all-in): base floor | 83.1223 | 92.9274 | 107.7651 | Primary negotiation zone width
Zone vs Ceiling B (energy-only): base floor | -7.6951 | 2.11 | 16.9477 | Zone if DC ignores its T&D savings (narrow-frame negotiation)
Zone vs Ceiling A: gross floor (no credit) | 51.7801 | 66.0875 | 81.3526 | Stress: zone survives loss of tax credits?
SEC 3: VIABILITY TESTS
| Solar+BESS | Wind+BESS | Geo+BESS | Reading
Viable vs all-in ceiling (base floor)? | YES | YES | YES | Framework 4.2 test
Viable vs energy-only ceiling (base floor)? | NO | YES | YES | If NO: developer's cost exceeds market PPA: only viable if DC shares its T&D savings
Viable vs all-in ceiling (zero credit)? | YES | YES | YES | Survives OBBBA Scenario D?
Model 2 BTM input ($60) above base floor? | NO: below LCOE | NO: below LCOE | YES | Consistency check: Model 2's $60 BTM assumption vs this model's floor. NO means Model 2 is pricing that config below cost.

## M4_Pricing
Model 4: BTM Price Setting and Two-Sided Viability Test
Three methods from framework Sec 4.3. Yellow lever = bargaining share α. Output feeds back to Model 2 (BTM revenue) and Model 3 (Structure C cost).
SEC 1: LEVERS
Bargaining share α (0 = DC has all power → floor; 1 = developer → ceiling) | 0.5 | frac | Framework 4.3: geothermal/unique site → α higher; DC with multiple site options → α lower. 0.5 = symmetric.
Industry discount to energy-only PPA | 15% | frac | Framework 4.3: 'BTM PPA typically set at 10-20% discount to grid PPA'. Midpoint 15%.
Developer levered IRR hurdle | 10% | frac | Framework 2.9.3: 'Developer equity hurdle rate: 10-15%'. Low end used.
DC minimum savings vs grid (H2 lower bound) | 20% | frac | H2 hypothesis: 20-35% savings. Lower bound as acceptance threshold.
SEC 2: THREE PRICE-SETTING METHODS ($/MWh)
| Solar+BESS | Wind+BESS | Geo+BESS | Method
Method 1: Midpoint (floor, all-in ceiling) | 121.2562 | 116.3537 | 108.9349 | Framework 4.5 Step 1: 'initial BTM price as midpoint of LCOE and Grid PPA'. Splits the full surplus 50/50.
Method 2: Industry discount to energy PPA | 61.2 | 61.2 | 61.2 | Framework 4.3 convention. Config-independent: ignores developer's cost. Matches Model 2's $60 at 17% discount.
Method 3: Bargaining share α on zone | 121.2562 | 116.3537 | 108.9349 | General form; Method 1 is α=0.5. Lever above.
Method 2 vs floor: is discount price above LCOE? | NO: below cost | NO: below cost | YES | If NO, the industry convention would price this config below its own LCOE. Developer would not sign.
SEC 3: SELECTED BTM PRICE (feeds Model 2 / Model 3)
Method selector (1/2/3) | 3 |  | Default = 3 (bargaining share). Change to 1 or 2 to switch.
BTM PPA price: selected ($/MWh) | 121.2562 | 116.3537 | 108.9349 | → Replace Inputs!B19 ($60 flat) with these per-config values to close the M4→M2 loop. Not auto-linked: Model 2 v7 has a single global BTM cell.
vs Model 2 current input ($60) | 61.2562 | 56.3537 | 48.9349 | Positive = Model 4 says price should be higher than Model 2 assumes.
SEC 4: TWO-SIDED VIABILITY AT SELECTED PRICE
| Solar+BESS | Wind+BESS | Geo+BESS | Test
Developer side: price − LCOE floor ($/MWh) | 41.5612 | 46.4637 | 53.8825 | Margin over cost at 8% WACC. Positive = earns above WACC unlevered.
Developer side: Model 2 co-loc levered IRR (live, at effective BTM) | 11.79% | 24.44% | 33.08% | Live from Model 2 at the effective BTM price (Configurations R16). With Inputs!B27 = 2 this IS the test at the Model 4 price; loop closed.
Developer side: meets hurdle at effective BTM? | YES | YES | YES
DC side: all-in BTM cost, Phase 2 ($/MWh) | 120.7385 | 121.3533 | 117.4229 | Recomputes M3_StructC Phase 2 formula at the selected BTM price instead of M3's $62 placeholder.
DC side: savings vs Structure B all-in | 25.84% | 25.47% | 27.88%
DC side: meets minimum savings? | YES | YES | YES
BOTH PARTIES VIABLE (Phase 2, at effective BTM)? | YES | YES | YES | Framework 4.5 Step 4: 'range of BTM prices that simultaneously satisfy both parties'. Requires: IRR ≥ hurdle AND DC savings ≥ min AND price ≥ LCOE.
SEC 5: PRICE RANGE SATISFYING BOTH (analytical)
Max price DC accepts (savings = min) | 154.1941 | 132.5366 | 122.2084 | Solves Phase-2 cost equation for P such that DC savings exactly equal the minimum threshold.
Min price developer accepts (LCOE floor) | 79.6951 | 69.89 | 55.0523
Mutually acceptable range width ($/MWh) | 74.4991 | 62.6466 | 67.156 | Negative = no price satisfies both at these thresholds. This is the headline Model 4 output.
Deal exists? | YES | YES | YES

## M4_Notes
Model 4: Methodology Notes and Findings
§1 What Model 4 does
Determines the price range within which a behind-the-meter PPA is acceptable to both the renewable developer and the co-located data center (framework Sec 4). Floor = developer's LCOE (M4_LCOE, computed from Model 2 Configurations at the Model 2 discount rate). Ceiling = data center's grid alternative (M3 Structure B all-in delivered cost). Zone = ceiling − floor. Three price-setting methods (framework 4.3/4.5), a two-sided viability test, and an analytical solve for the mutually acceptable range.
§2 LCOE construction
Closed-form: LCOE = [CAPEX + OPEX × PVA(r,N)] / [E₁ × q(1−q^N)/(1−q)] with q = (1−d)/(1+r). CAPEX and OPEX pulled live from Configurations (NREL ATB 2024 midpoints). Discount rate linked to Model 2's 8% NPV rate (framework 2.4: WACC 7–9%). Two variants: gross (no credits, OBBBA Scenario D) and net of tax equity (CAPEX reduced by the Capitalization R18 contribution). Net LCOE is the base floor because tax equity is real capital the developer does not have to raise. Model LCOEs are above NREL ATB generation-only ranges because they include BESS (LCOS $113–159), microgrid, land, and interconnection: this is by design; the floor must cover the whole project.
§3 FINDING: Model 2's $60/MWh BTM price is below LCOE for solar and wind
Base-case co-location LCOE net of tax equity: Solar $79.70, Wind $69.89, Geothermal $55.05. Model 2 v7 uses a flat $60 BTM input for all three. At $60, solar is selling ~$20 below cost and wind ~$10 below cost at 8% WACC; only geothermal clears its floor. This is consistent with Model 2's own unlevered IRRs (solar 1.3%, wind 2.6%, geo 5.0% co-loc: all below 8%) and with the earlier finding that solar cannot be rescued by co-location. The $60 figure came from the 'industry 10–20% discount to energy PPA' convention, which is benchmarked to the $72 energy-only PPA and is blind to the developer's cost.
§4 FINDING: the true negotiation zone is much wider than the framework expected, because the ceiling is higher
Framework Sec 3 estimated Structure B (sleeved grid PPA) at $60–90/MWh. Model 3 found $162.82 once RA ($45), TAC ($16), NBC ($23), and shaping are stacked. That $91 gap between energy-only PPA and all-in delivered cost is the 'T&D + capacity savings pool' the two parties are actually dividing. With the all-in ceiling, the zone is $83 (solar) / $93 (wind) / $108 (geo) wide, and the midpoint price is ~$109–121 rather than ~$60. At the midpoint the developer earns $42–54/MWh over LCOE and the DC still saves 26–28% vs grid: both parties clear their thresholds for all three configurations. Framework 4.2's warning that 'if LCOE > Grid PPA Cost, co-location is not viable' does NOT bind for any configuration once the correct ceiling is used, even in the zero-credit stress case.
§5 FINDING: Method 2 (industry convention) and Methods 1/3 (surplus-splitting) give very different prices; the paper must choose and justify
Method 2 gives $61 for all configs (config-blind). Methods 1/3 at α=0.5 give $109–121 (config-specific). The $50–60 gap is the T&D savings pool split. Recommended framing for the paper: Method 2 is what a DC would open with if it frames the deal as 'a cheaper PPA'; Methods 1/3 are what the deal is worth once the DC's avoided wires and capacity costs are priced in. The bargaining lever α lets the paper show the full range. A defensible base case is α = 0.5 (framework 4.3: 'allocating the T&D savings roughly 50/50'), which is Method 1.
§6 Analytical mutually-acceptable range (SEC 5)
P_max is solved from the Model 3 Phase-2 cost equation: P such that DC all-in cost = Ceiling_A × (1 − min_savings). P_min is the LCOE floor. Range width: Solar $74.50, Wind $62.65, Geo $67.16: a deal exists for all three at 20% minimum DC savings and 8% developer WACC. Solar's range is widest because its low coverage ratio (29%) means the BTM price has little weight in the DC's blended cost, so the DC is price-insensitive to it. This is a double-edged result: the DC will accept a high solar BTM price, but the developer earns it on only 29% of the DC's load.
§7 What is NOT closed in this iteration
(a) The M4→M2 loop is not auto-linked: Model 2 v7 has a single global BTM cell (Inputs!B19). To close the loop, set B19 to each config's selected price in turn and read the levered IRR: or add a per-config BTM row to Model 2. (b) The IRR shown in M4_Pricing SEC 4 is Model 2's live value at $60, not at the selected price; it is a proxy. (c) LCOE uses 8% flat; a config-specific WACC (geothermal lower risk → lower WACC → lower floor) would widen the geothermal zone further. (d) Bargaining share α is a lever, not an estimate: practitioner interviews (Q4 in Chien questions, tax-equity market conditions) are the intended source. (e) Carbon scenarios from M1 are not yet wired into the ceiling; C30/C60 would raise Ceiling_C by $13/$26 and Ceiling_A by roughly the same (higher spot passes through to the sleeved PPA).
§8 Implication for H1/H2 restatement
H1 (developer IRR +3–6 pp) was tested in Model 2 at $60 BTM. At Model-4-consistent prices, the co-location uplift is larger for all configs and solar likely crosses the 10% hurdle. H2 (DC saves 20–35%) holds at the midpoint price for all configs in Phase 2 (26–28%). The restated hypothesis should be joint: 'there exists a BTM price at which the developer clears WACC and the DC saves ≥20%, for all three configurations, with the geothermal zone widest on the developer side and the solar zone widest on the DC side.'

## Fig2_Breakeven
Figure 2 data: developer levered IRR vs post-completion queue wait
STATIC VALUES. Each row is one full model run (Inputs!B5 = queue years, B6 = ITC, B27 = BTM lever), IRR recomputed from the developer cash-flow column (K5:K37) with numpy_financial because LibreOffice IRR() does not converge for negative returns. Regenerate with the sweep script if any upstream input changes. Levers: 1 = flat $60 BTM (Inputs!B19), 2 = Model 4 per-config price. Columns J-L record the effective BTM price for each row; under lever 2 it rises when ITC = 0 because the LCOE floor loses its tax-equity offset.
BTM lever | ITC | Queue (yr) | Solar base | Solar coloc | Wind base | Wind coloc | Geo base | Geo coloc | Solar BTM $/MWh | Wind BTM $/MWh | Geo BTM $/MWh
1 | 30% | 1 | 9.204% | 5.234% | 14.26% | 11.7% | 19.22% | 20.91% | 60 | 60 | 60
1 | 30% | 2 | 6.982% | 4.935% | 11.33% | 11.07% | 15.72% | 20.06% | 60 | 60 | 60
1 | 30% | 3 | 5.356% | 4.661% | 9.247% | 10.53% | 13.35% | 19.38% | 60 | 60 | 60
1 | 30% | 4 | 4.071% | 4.407% | 7.647% | 10.06% | 11.61% | 18.82% | 60 | 60 | 60
1 | 30% | 5 | 2.614% | 4.079% | 5.875% | 9.487% | 9.767% | 18.18% | 60 | 60 | 60
1 | 30% | 6 | 1.397% | 3.773% | 4.427% | 8.98% | 8.32% | 17.64% | 60 | 60 | 60
1 | 30% | 7 | 0.3388% | 3.484% | 3.191% | 8.523% | 7.132% | 17.18% | 60 | 60 | 60
1 | 30% | 8 | -0.6133% | 3.21% | 2.1% | 8.107% | 6.122% | 16.79% | 60 | 60 | 60
1 | 0% | 1 | -0.1728% | -1.008% | 2.276% | 1.34% | 5.479% | 5.735% | 60 | 60 | 60
1 | 0% | 2 | -0.8374% | -1.143% | 1.488% | 1.161% | 4.693% | 5.566% | 60 | 60 | 60
1 | 0% | 3 | -1.443% | -1.276% | 0.7868% | 0.9891% | 4.017% | 5.409% | 60 | 60 | 60
1 | 0% | 4 | -2.006% | -1.408% | 0.1462% | 0.8223% | 3.419% | 5.263% | 60 | 60 | 60
1 | 0% | 5 | -2.539% | -1.54% | -0.4506% | 0.6599% | 2.879% | 5.127% | 60 | 60 | 60
1 | 0% | 6 | -3.052% | -1.671% | -1.016% | 0.5009% | 2.384% | 4.998% | 60 | 60 | 60
1 | 0% | 7 | -3.552% | -1.802% | -1.561% | 0.3446% | 1.922% | 4.876% | 60 | 60 | 60
1 | 0% | 8 | -4.047% | -1.934% | -2.092% | 0.1902% | 1.486% | 4.761% | 60 | 60 | 60
2 | 30% | 1 | 9.204% | 6.983% | 14.26% | 15.56% | 19.22% | 25.53% | 121.26 | 116.35 | 108.93
2 | 30% | 2 | 6.982% | 8.555% | 11.33% | 18.9% | 15.72% | 28.7% | 121.26 | 116.35 | 108.93
2 | 30% | 3 | 5.356% | 10.2% | 9.247% | 21.97% | 13.35% | 31.22% | 121.26 | 116.35 | 108.93
2 | 30% | 4 | 4.071% | 11.79% | 7.647% | 24.44% | 11.61% | 33.08% | 121.26 | 116.35 | 108.93
2 | 30% | 5 | 2.614% | 13.8% | 5.875% | 27% | 9.767% | 34.91% | 121.26 | 116.35 | 108.93
2 | 30% | 6 | 1.397% | 15.49% | 4.427% | 28.8% | 8.32% | 36.16% | 121.26 | 116.35 | 108.93
2 | 30% | 7 | 0.3388% | 16.84% | 3.191% | 30.06% | 7.132% | 37.02% | 121.26 | 116.35 | 108.93
2 | 30% | 8 | -0.6133% | 17.9% | 2.1% | 30.94% | 6.122% | 37.61% | 121.26 | 116.35 | 108.93
2 | 0% | 1 | -0.1728% | -0.1251% | 2.276% | 2.435% | 5.479% | 6.682% | 136.93 | 129.77 | 122.14
2 | 0% | 2 | -0.8374% | 0.7145% | 1.488% | 3.446% | 4.693% | 7.479% | 136.93 | 129.77 | 122.14
2 | 0% | 3 | -1.443% | 1.639% | 0.7868% | 4.538% | 4.017% | 8.287% | 136.93 | 129.77 | 122.14
2 | 0% | 4 | -2.006% | 2.627% | 0.1462% | 5.669% | 3.419% | 9.08% | 136.93 | 129.77 | 122.14
2 | 0% | 5 | -2.539% | 3.641% | -0.4506% | 6.786% | 2.879% | 9.835% | 136.93 | 129.77 | 122.14
2 | 0% | 6 | -3.052% | 4.637% | -1.016% | 7.84% | 2.384% | 10.53% | 136.93 | 129.77 | 122.14
2 | 0% | 7 | -3.552% | 5.578% | -1.561% | 8.795% | 1.922% | 11.16% | 136.93 | 129.77 | 122.14
2 | 0% | 8 | -4.047% | 6.434% | -2.092% | 9.634% | 1.486% | 11.71% | 136.93 | 129.77 | 122.14

## Fig3_Zone
Figure 3 data: BTM price bounds and mutually acceptable range
LIVE. All values link to M4_Bounds / M4_Pricing. Stacked bar: segment 1 (no fill) = floor offset; segment 2 (green) = mutually acceptable range; segment 3 (grey) = remainder of zone to ceiling.
Configuration | Net LCOE floor | Gross LCOE | DC 20% limit (P_max) | Ceiling (Structure B) | Midpoint | Seg1: floor | Seg2: acceptable | Seg3: rest of zone | $60 marker
Solar+BESS 100 MW | 79.6951 | 111.0374 | 154.1941 | 162.8174 | 121.2562 | 79.6951 | 74.4991 | 8.6233 | 60
Wind+BESS 150 MW | 69.89 | 96.73 | 132.5366 | 162.8174 | 116.3537 | 69.89 | 62.6466 | 30.2808 | 60
Geothermal+BESS 100 MW | 55.0523 | 81.4648 | 122.2084 | 162.8174 | 108.9349 | 55.0523 | 67.156 | 40.609 | 60

## Fig4_Alpha
Figure 4 data: two-sided viability across the bargaining share
STATIC VALUES from 7 closed-loop runs varying M4_Pricing!B5 (α). IRR = Results!B5:D5 (live Model 2 at that price); DC saving = M4_Pricing DC-side savings row. Regenerate if upstream inputs change. Hurdle 10% and min saving 20% are the M4_Pricing lever values.
α | Solar IRR | Solar DC saving | Wind IRR | Wind DC saving | Geo IRR | Geo DC saving | Hurdle | Min saving
0 | 6.27% | 33.22% | 11.87% | 41.16% | 17.73% | 59.87% | 10% | 20%
0.1 | 7.189% | 31.74% | 13.87% | 38.02% | 20.22% | 53.47% | 10% | 20%
0.2 | 8.197% | 30.27% | 16.16% | 34.88% | 23.07% | 47.08% | 10% | 20%
0.35 | 9.888% | 28.06% | 20.11% | 30.18% | 27.9% | 37.48% | 10% | 20%
0.5 | 11.79% | 25.84% | 24.44% | 25.47% | 33.08% | 27.88% | 10% | 20%
0.65 | 13.9% | 23.63% | 28.88% | 20.76% | 38.28% | 18.28% | 10% | 20%
0.8 | 16.15% | 21.42% | 33.22% | 16.05% | 43.29% | 8.686% | 10% | 20%